EVIDENCE PACKAGE

Garage GFCI receptacle below required elevation

Cooper Residence Renovation / CR-2026-017 / BUI-1042

| Priority | Classification | Evidence | Control |
| --- | --- | --- | --- |
| HIGH | UNAPPROVED DEVIATION | SUFFICIENT | DRAFT |

# Verification finding

| Observed | Required / expected | Difference |
| --- | --- | --- |
| GFCI box centerline measures 12 inches above finished floor at the garage east wall. | E1.1 Electrical Note 3 requires garage receptacle centerline at a minimum 18 inches AFF. | Installed centerline is 6 inches below the explicit approved drawing requirement. |

## Recommended route

| Route | Reviewer note |
| --- | --- |
| FIELD CORRECTION PUNCH | Installed centerline is 6 inches below the explicit approved drawing requirement. |

# Evidence register

| Type | Evidence | Location / capture |
| --- | --- | --- |
| PHOTO | Garage east wall context Open stud wall near the garage entry door; GFCI rough-in visible. | Building: Residence / Space: Garage / Wall: East wall / Near: Entry door 2026-07-12T10:18:00-07:00 |
| MEASUREMENT | GFCI centerline tape measurement Tape shows receptacle centerline at approximately 12 inches AFF. | Building: Residence / Space: Garage / Wall: East wall / Near: Entry door 2026-07-12T10:18:20-07:00 |
| PHOTO | Receptacle rough-in detail Close view of the installed box before wall close-in. | Building: Residence / Space: Garage / Wall: East wall / Near: Entry door 2026-07-12T10:18:38-07:00 |

## Field image review

Garage east wall context / Building: Residence / Space: Garage / Wall: East wall / Near: Entry door

GFCI centerline tape measurement / Building: Residence / Space: Garage / Wall: East wall / Near: Entry door

Receptacle rough-in detail / Building: Residence / Space: Garage / Wall: East wall / Near: Entry door

# Source index

Every requirement statement must be checked against the exact document revision below. Superseded or unapproved sources cannot authorize work.

| # | Document / revision | Page | Cited requirement |
| --- | --- | --- | --- |
| 1 | E1.1 / Rev IFC-1 / APPROVED SHA-256: 50be9d19503471862a14e1383cbb5c4cf04a8cd97c237521cc324221e104bec1 | 1 | Electrical Note 3: Garage receptacle centerline shall be minimum 18 inches above finished floor. |

# Review control

| Report ID | Version | Generated | Status |
| --- | --- | --- | --- |
| rpt_demo_bui_1042 | 1 | 2026-07-12 17:25 UTC | DRAFT / REVIEW REQUIRED |

BUILI assembles a traceable review record. It does not make a design decision, authorize a change, determine contractual entitlement, or replace review by the responsible architect, engineer, contractor, or authority having jurisdiction.