PUNCH ITEM

Raise garage GFCI rough-in before wall close-in

Cooper Residence Renovation / CR-2026-017 / P-024

| Responsible trade | Punch manager | Final approver | Due date |
| --- | --- | --- | --- |
| Delta Electrical | Jordan Cho / Project Manager | Jordan Cho / Project Manager | 2026-07-14 |

## Deficiency

Deficiency

GFCI box centerline measures 12 inches above finished floor at the garage east wall.

## Contract requirement

Contract requirement

E1.1 Electrical Note 3 requires garage receptacle centerline at a minimum 18 inches AFF.

## Required correction

Required correction

Relocate the box so its centerline is at least 18 inches AFF before gypsum board installation.

## Completion proof

Completion proof

Provide a completion photo showing the full wall context and a readable tape measurement from finished floor to box centerline.

## Activity and chronology

| Time | Actor | Event |
| --- | --- | --- |
| 2026-07-12 10:18 PDT | Mike Alvarez | Field observation and three evidence assets captured. |
| 2026-07-12 10:24 PDT | BUILI | E1.1 Rev 03 requirement linked; evidence package marked sufficient. |

# Evidence register

| Type | Evidence | Location / capture |
| --- | --- | --- |
| PHOTO | Garage east wall context Open stud wall near the garage entry door; GFCI rough-in visible. | Residence / Garage / East wall / Entry door 2026-07-12T10:18:00-07:00 |
| MEASUREMENT | GFCI centerline tape measurement Tape shows receptacle centerline at approximately 12 inches AFF. | Residence / Garage / East wall / Entry door 2026-07-12T10:18:20-07:00 |
| PHOTO | Receptacle rough-in detail Close view of the installed box before wall close-in. | Residence / Garage / East wall / Entry door 2026-07-12T10:18:38-07:00 |

## Field image review

Garage east wall context / Residence / Garage / East wall / Entry door

GFCI centerline tape measurement / Residence / Garage / East wall / Entry door

Receptacle rough-in detail / Residence / Garage / East wall / Entry door

# Source index

Every requirement statement must be checked against the exact document revision below. Superseded or unapproved sources cannot authorize work.

| # | Document / revision | Page | Cited requirement |
| --- | --- | --- | --- |
| 1 | E1.1 / Rev 03 / APPROVED SHA-256: 85dceb1e6df4016fed87d520fd9c22a6049e351927123c6b587d697310a77fda | 1 | Electrical Note 3: Garage receptacle centerline shall be minimum 18 inches above finished floor. |

# Review control

| Report ID | Version | Generated | Status |
| --- | --- | --- | --- |
| rpt_demo_p024 | 1 | 2026-07-12 17:25 UTC | DRAFT / REVIEW REQUIRED |

BUILI assembles a traceable review record. It does not make a design decision, authorize a change, determine contractual entitlement, or replace review by the responsible architect, engineer, contractor, or authority having jurisdiction.